Tonhe Timer Instruction

1 Parameter specifies

Working voltage :110～250VDC(110～230VAC)

The time for keeping valve open :0 H : 0M :0S --99 H 59 M 59 S

The time for keeping valve closed : 0 H : 0M :0S --99 H 59 M 59 S

2 Timer specification

Set button, Location selection button,   Increasing button

4 digital time display

Position indicator

3 Operation instruction

Actuator parameter setting have two menu structures on below:

Function code ( fist menu),

The setting parameters of function code ( secondary menu)

Normal operation

First  menu

Secondary  menu

Picture 0 Secondary menu operation menu

| Function code | Content | Value | Unit | Remarks |
| --- | --- | --- | --- | --- |
| t on | valve keeping open time open | 00:00:00 – 99:59:59 | H:M:S |  |
| toFF | valve keeping closed time | 00:00:00 – 99:59:59 | H:M:S |  |
| PonS | Power -on Action | On/off |  |  |
| Prot | Stall current setting | 0-599 | MA | When the current is bigger than the setting value 1.6S, the motor will stop working , and the display will show Err. |

Parameter function control table

Picture 1                     picture 2

1  Press  2 seconds and enter to fist menu, the screen display picture 1 text（t on） , indicating enter to set the valve keeping open state .

Pressagain, the screen display picture 2 text （t o FF）,indicating enter to set the valve keeping closed state .

Picture 3                     picture 4

2  Press then the  after entering the stetting state , showing the valve keeping time for setting ( Set the valve keeping open time on the valve keeping open state . Set the valve keeping closed time on the valve keeping closed state.) . Select flashing bit by pressing, and change the numerical by pressing.

When " : " is flashing , indicate setting "HS ( hours) :MS(minutes)", and change the flashing fit by pressing.

When the " : " is bright , indicate setting " MS(minutes) :SS(seconds) " .

The data will be deposited in the valve controller after completing the setting .

Press  when finish setting , will return fist menu , press  again , enter to next fist menu to set parameters .

Picture 5                          picture 6

3 Press the&, the screen display picture 5 , indicating open the valve manually.

Press the&, the screen display picture 6, indicating closed the valve manually .

Exit manual mode to press the& or &. And go the power -on action .

Picture 7                           picture 8

4 On the normal working state, the displayed time is valve keeping time.(e.g. Valve keeping open time is 10 S, will count down 10S)

The " : " is flashing , indicating the "HS ( hours) : MS(minutes)"' .

The " : " is bright, indicating the " MS(minutes) : SS(seconds) " .

4 Stalling protection function

When the actuator is detected stalling, it will run in reverse direction .when reach to the open or closed position , and do the close or open action again , meanwhile displaying flashed 0000-0001 on screen ( indicating the current retrying times ) . If it fail at third retrying , the valve will stop running and display ERRL on the screen .